222 Church St. S., Alliston , ON • Phone: 905.857.4700 • www.alumavent.com

# product specification guide

## model SERIES 3900 INSULATED THERMAL-BREAK control damper

# Service Subgroup: Division 23, HVAC (Formerly Division 15)

***************************************************************************************************************

Information contained herein is protected by copyright and is proprietary to Alumavent Inc., who authorizes the user limited non-exclusive permission to use this document or portions of it for the purpose of preparing written product specifications for the above CSI MasterFormat division. All information in this document as provided by Alumavent Inc. is informational in nature and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, any implied warranty or non-infringement. As permitted by applicable law, Alumavent Inc. assumes no liability, and user assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether as modified by the user or not. Users should consult www.alumavent.com to verify that this document represents the most up-to-date version.

Specifier Notes: This product guide specification is written according to the Construction Specifications Institute (CSI) Format - 2004 Edition.

The section must be carefully reviewed and edited by the engineer to meet the requirements of the project and local building code. Coordinate with other specification sections and the drawings.

Delete all unnecessary "Specifier Notes" when editing this section.

## ***************************************************************************************************************

## PART 1: GENERAL

  - WORK INCLUDED

- Extruded aluminum insulated control dampers assembled with integral thermally broken frame and blades suitable for application in HVAC systems with velocities up to 3000 feet per minute (15.2 m/s)

  - RELATED WORK

- *****************************************************************************************************

- Specifier Notes: Edit the following list as required for the project. List other sections with work directly related to the dampers. *****************************************************************************************************

- Section 23 30 00 HVAC Air Distribution.

1.3	REFERENCES

- *****************************************************************************************************

- Specifier Notes: List standards referenced in this section, complete with designations and titles. This article does not require compliance with standards, but is simply a listing of those used. *****************************************************************************************************

- AMCA 500-D – Laboratory Methods for Testing Dampers for Ratings.

- AMCA 511 – Certified Ratings Program for Air Control Devices.

- IECC - International Energy Conservation Code.

- ASHRAE Standard 62 – Ventilation for Acceptable Indoor Air Quality

1.4	SUBMITTALS

- Comply with requirements of Section 23 33 00 – Submittal Procedures.

- Product Data: Submit manufacturer’s product data.

- Include leakage, pressure drop, maximum velocity and pressure data

- Indicate materials, construction, and dimensions.

- Include pressure drop data for all damper sizes in accordance with AMCA 500-D Test Figure 5.3 (Ducted Inlet, Ducted Outlet).

- Include a copy of installation, operation and maintenance instructions.

  - QUALITY ASSURANCE

A.          Dampers shall be thoroughly inspected and cycled in the factory to ensure proper operation.

  - DELIVERY, STORAGE, AND HANDLING

- Delivery: Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly indicating manufacturer, material, and location of installation.

- Storage: Store materials in a dry area indoor, protected from damage, and in accordance with manufacturer’s instructions.

- Handling: Handle and lift dampers in accordance with manufacturer’s instructions. Protect materials and finishes during handling and installation to prevent damage.

## PART 2:  PRODUCTS

2.1	MANUFACTURER

- Alumavent Inc. 222 Church St. S., Alliston, Ontario, L9R 2B7. Phone: 905.857.4700                 Fax: 905.857.4730 Web Site: www.alumavent.com.

  - HVAC Control Damper

- Model Series: 3900 Insulated Thermal-Break Control Damper

- Ratings

- Leakage:

- ********************************************************************************************

- Dampers shall have a maximum leakage of 3 cfm/sq. ft. @ 1” w.g., 8 cfm/sq. ft. @ 4” w.g. and 11 cfm/sq. ft. @ 8” w.g. and shall be AMCA Certified.

- Damper shall meet or exceed the IECC (International Energy Conservation Code) building envelope requirements for maximum damper leakage ratings of 3 cfm/sq. ft. @ 1” w.g. or 8 cfm/sq. ft. @ 4” w.g.

- Differential Pressure:

- ********************************************************************************************

- Dampers shall have a maximum differential pressure rating of 8” w.g. (2 kPa), or less, dependent on damper single section width.

- Velocity:

- ********************************************************************************************

- Dampers shall have a maximum velocity rating of 3000 fpm (15.2 m/s).

- Construction:

- Frame:

- ********************************************************************************************

Specifier Note: The following requirements for frame construction provide for specific corner assembly type. A major problem with dampers is thin or non-rigid construction resulting in damper operating problems because they are installed out of square or racked. Butt-corner assembly required by the following specification will minimize these problems.

- ********************************************************************************************

Frame shall be 4-piece construction assembled with butt type joining at corners to assure square corners and provide maximum resistance to racking.

□   Model 3965 flange-to-duct damper frame shall be extruded aluminum, 4" deep x 1"                                          structural U-channel.

□   Model 3961 in-duct mount frame shall be extruded aluminum, 5-1/4” deep hat channel style.

- Blades:

- ********************************************************************************************

Specifier Notes: The following requirements for blade construction incorporate a variable symmetrical blade design. Many damper manufacturers utilize non-symmetrical blades to accommodate varying damper heights. When blades are non-symmetrical, resulting operating torque varies significantly depending on direction of airflow through the damper. As well, larger blade stops at bottom and top of damper are required. This reduces damper free area and results in higher pressure loss across the damper.

- ********************************************************************************************

Blades: Damper blades shall be heavy gauge extruded aluminum airfoil shape with blade to blade overlap and shall be of true thermally broken construction with minimum R-2.25 non-CFC polyurethane foam insulation. Each blade shall be symmetrical relative to its axle pivot point, presenting identical performance characteristics with air flowing in either direction through the damper. Provide symmetrical blades of varying size as required to completely fill the damper opening. Blade orientation is horizontal. Blade operation is parallel or opposed.

- Blade Stops:

- ********************************************************************************************

Specifier Notes: The following requirement for blade stop construction minimizes blade stop height. Large blade stops reduce damper free area and results in higher pressure loss across the damper.

- ********************************************************************************************

Each blade stop (at bottom and top of damper frame) shall occupy no more than 1” of the damper opening area to allow for maximum free area and to minimize pressure loss across the damper.

- Seals:

- Blade Edge: Blade seals shall be extruded Santoprene rubber mechanically locked into blade edge slots.

- Jamb: Extruded Santoprene rubber type locked in integral jamb slots.

- Linkage: Concealed in jamb.

- ********************************************************************************************

Specifier Notes: Linkage concealed in the jamb of the damper reduces pressure drop across the damper and results in less maintenance than on-blade-linkage.

- ********************************************************************************************

6.	Axles: Minimum 3/8” square aluminum. Stainless steel axles are optional.

7.	Bearings: Axle bearings shall be maintenance-free, 2-piece construction, Celcon inner bearing rotating within a polycarbonate outer sleeve inserted into extruded holes in the damper frame.

- ********************************************************************************************

Specifier Notes: Extruded bearing holes in frame provide more axle to bearing surface area. As a result, bearings will last longer and add to the life of the damper.

- ********************************************************************************************

8. 	Finish: Mill aluminum finish is standard. Clear anodized finish is optional.

- ********************************************************************************************

Specifier Notes: Standard finish is mill aluminum. Optional clear anodized finish provides extra resistance to corrosion for dampers that may come in contact with salt water air or other mildly corrosive applications.

- ********************************************************************************************

  - ACCESSORIES/OPTIONS

A.	Actuators:

- *****************************************************************************************************

Specifier Notes: Specify electric or pneumatic actuators. Specify external or internal mounting. Electric actuators and components are to be factory grounded to single point junction box in accordance with Part 1 of the Canadian Electrical Code (Rigid and Flexible Metal Conduit Rules) or the National Electrical Code. External mounting is recommended for ease of accessing for inspection and to minimize airflow blockage that will result in higher pressure drop across the damper. Specifier selects the required actuator type and mounting location:

- *****************************************************************************************************

- Type:

- Manual quadrant

- Electric, 120V AC, 2-position, spring return

- Electric, 24V AC, 2-position, spring return

- Electric, 230V AC, 2-position, spring return

- Pneumatic, 20 psi minimum control pressure, 2 position, spring return

- Mounting:

- External (out of airstream)

- Internal (in the airstream)

B. 	Auxiliary Position Indicating Switch

*******************************************************************************	Specifier Notes: Position Indicator Switch indicates blade position, either fully open or fully closed.

. 	*******************************************************************************

Optional two-position indicator switch is integral to the actuator when required.

C.	Thermally Broken Frame/Thermally Broken Flanged Frame

*******************************************************************************	Specifier Notes: Frame is thermally broken to minimize heat transfer. 	*******************************************************************************

□   Model 3965BF has 1” flange-to-duct extruded aluminum frame and thermally broken.

□   Model 3967BF has a larger flange on one side thermally broken frame.

*******************************************************************************

- Silicone Blade and Jamb Seals

*******************************************************************************

□   Model Series 3900SI: Silicone blade and jamb seals.

- Salt Water Construction

*******************************************************************************

□   Model 3900SW: Clear anodized blades and frame and stainless steel linkage/hardware.

  - SOURCE QUALITY CONTROL

- Factory Tests: Factory cycle damper and actuator assemblies to assure proper operation.

## PART 3:  EXECUTION

3.1	EXAMINATION

- Examine any areas where dampers may be received. Notify the engineer of any conditions that would adversely affect installation or subsequent utilization of dampers. Do not proceed with installation until unsatisfactory conditions are corrected.

3.2	INSTALLATION

- Install dampers in accordance with manufacturer’s installation instructions.

- Dampers must be accessible to allow inspection, adjustment, and replacement of components. The sheet metal contractor shall furnish any access doors in ductwork or plenums required to provide this access. The general contractor shall furnish any access doors required in walls, ceilings, or other general building construction.

- Install dampers square and free from racking.

- The installing contractor shall provide and install bracing for multiple section assemblies to support assembly weight and to hold against system pressure.

- Do not compress or stretch the damper frame into the duct or opening. Use shims as necessary.

- Attach multiple damper section assemblies together in accordance with manufacturer’s instructions. Install support mullions as reinforcement between assemblies as required.

- Handle dampers using the frame only. Do not lift or move dampers using blades, actuators or jackshafts.

- Install connections to electric or pneumatic actuators as specified in relative section and as required by local code.

# END OF SECTION